## Summary
LoRaWAN vs NB-IoT vs PoE — Cost & Fit Summary
UK planning benchmark • GBP ex VAT • 5-year default • category scenarios are independently editable
Model headline |  |  | What the model says
Categories modelled | 16 |  | PoE is now modelled as a third architecture, including endpoint hardware, cabling and installation, shared switch/network infrastructure, electricity, support and maintenance. Cost winners exclude options with a suitability score below 3. Blank device quantities remain deliberately unconfigured; enter units and sites in Category Model, then replace blue PoE assumptions with surveyed cable routes, spare-port capacity and vendor quotes.
Configured scenarios | 1
LoRaWAN lower-cost | 1
NB-IoT lower-cost | 1
PoE lower-cost | 0
Default horizon | 5
Sensor / use case | LoRa fit | NB fit | PoE fit | LoRa TCO/unit | NB TCO/unit | PoE TCO/unit | Lowest-cost viable | Technical recommendation | Confidence |  |  |  | Sensor / use case | LoRaWAN | NB-IoT | PoE
IAQ sensors | 5 | 4 | 5 | 284.05 | 356 | 462 | LoRaWAN | LoRaWAN for dense estates; NB-IoT for isolated buildings | Medium | IAQ sensors | 5 | 284.05 | IAQ sensors | 284.05 | 356 | 462
People counting / footfall | 4 | 4 |  | #DIV/0! | #DIV/0! |  | NB-IoT | Either; choose by estate density and power availability | Medium | People counting / footfall | #DIV/0! | #DIV/0!
Parking bay sensors | 5 | 5 | 2 |  |  |  | Not modelled | Enter device quantity in Category Model | Medium | Parking bay sensors | 2 |  | Parking bay sensors
Room displays | 3 | 3 | 5 |  |  |  | Not modelled | Enter device quantity in Category Model | Low | Room displays | 5 |  | Room displays
Lux sensors | 5 | 4 | 5 |  |  |  | Not modelled | Enter device quantity in Category Model | Medium | Lux sensors | 5 |  | Lux sensors
Metering — electricity and water | 5 | 5 | 4 |  |  |  | Not modelled | Enter device quantity in Category Model | High | Metering — electricity and water | 4 |  | Metering — electricity and water
Fridge / process temperature | 5 | 5 | 4 |  |  |  | Not modelled | Enter device quantity in Category Model | High | Fridge / process temperature | 4 |  | Fridge / process temperature
Waste water monitoring | 4 | 5 | 2 |  |  |  | Not modelled | Enter device quantity in Category Model | Medium | Waste water monitoring | 2 |  | Waste water monitoring
Water temperature | 5 | 5 | 3 |  |  |  | Not modelled | Enter device quantity in Category Model | High | Water temperature | 3 |  | Water temperature
Water flow | 5 | 5 | 3 |  |  |  | Not modelled | Enter device quantity in Category Model | High | Water flow | 3 |  | Water flow
Water leak detection | 5 | 5 | 4 |  |  |  | Not modelled | Enter device quantity in Category Model | High | Water leak detection | 4 |  | Water leak detection
Acoustic sensors | 4 | 5 | 4 |  |  |  | Not modelled | Enter device quantity in Category Model | Medium | Acoustic sensors | 4 |  | Acoustic sensors
Bin fill level — ultrasonic | 5 | 5 | 2 |  |  |  | Not modelled | Enter device quantity in Category Model | High | Bin fill level — ultrasonic | 2 |  | Bin fill level — ultrasonic
Optical bin sensors / computer vision | 2 | 2 | 5 |  |  |  | Not modelled | Enter device quantity in Category Model | Low | Optical bin sensors / computer vision | 5 |  | Optical bin sensors / computer vision
Vibration sensors | 4 | 4 | 5 |  |  |  | Not modelled | Enter device quantity in Category Model | Medium | Vibration sensors | 5 |  | Vibration sensors
Pressure sensors — medical gases | 4 | 4 | 5 |  |  |  | Not modelled | Enter device quantity in Category Model | Low | Pressure sensors — medical gases | 5 |  | Pressure sensors — medical gases
Ultrasonic non-invasive — medical gases | 4 | 4 | 5 |  |  |  | Not modelled | Enter device quantity in Category Model | Low |  |  |  | Ultrasonic non-invasive — medical gases

## Assumptions
LoRaWAN vs NB-IoT vs PoE — Planning Assumptions | LoRaWAN vs NB-IoT — Planning Assumptions | LoRaWAN vs NB-IoT — Planning Assumptions | LoRaWAN vs NB-IoT — Planning Assumptions | LoRaWAN vs NB-IoT — Planning Assumptions | LoRaWAN vs NB-IoT — Planning Assumptions
Blue cells are editable. Costs exclude VAT and the business application/dashboard layer common to all options. | Blue cells are editable. Costs exclude VAT and the business application/dashboard layer common to both options. | Blue cells are editable. Costs exclude VAT and the business application/dashboard layer common to both options. | Blue cells are editable. Costs exclude VAT and the business application/dashboard layer common to both options. | Blue cells are editable. Costs exclude VAT and the business application/dashboard layer common to both options. | Blue cells are editable. Costs exclude VAT and the business application/dashboard layer common to both options.
Driver | Value | Unit | Basis | Source / evidence | Sensitivity note
Analysis horizon | 5 | years | Planning assumption |  | Change to 3, 7 or 10 years as required
Gateways per site | 1 | gateway/site | Planning assumption |  | Survey RF coverage; resilient designs may need 2+
LoRaWAN gateway hardware | 415.8 | £/gateway | Milesight UG65 UK price | https://ukiot.io/shop/ | Lower-cost gateways start around £190
LoRaWAN gateway installation | 300 | £/gateway | Planning allowance |  | Includes mounting, power and network connection
LoRaWAN gateway support | 60 | £/gateway/year | Planning allowance |  | Remote monitoring and firmware administration
LoRaWAN gateway power | 22 | £/gateway/year | 8 W at £0.31/kWh |  | Remove if hosted power is immaterial
LoRaWAN network server | 0 | £/device/month | Planning benchmark at scale | https://aws.amazon.com/marketplace/pp/prodview-djx65iyt6w5cy | Small fleets can face a fixed minimum; embedded/open-source can be lower
LoRaWAN fixed platform charge | 0 | £/deployment/year | Assumes shared or embedded server |  | Enter vendor minimum subscription if applicable
LoRaWAN device commissioning | 15 | £/device | Planning allowance |  | Provisioning, keys, labelling and acceptance
NB-IoT monthly connectivity | 0.98 | £/device/month | User-provided tariff |  | Applied for every month in the analysis horizon
NB-IoT SIM / activation one-off fee | 0.7 | £/device | User-provided tariff |  | Charged once per device
NB-IoT included data | 17 | MB/device/month | User-provided tariff |  | Monthly allowance; overage is charged separately
NB-IoT data overage | 0.01 | £/MB | User-provided tariff |  | Applied to monthly usage above 17 MB per device
NB-IoT device commissioning | 12 | £/device | Planning allowance |  | SIM/eSIM activation and acceptance
Annual device maintenance | 2 | % of hardware/year | Planning allowance |  | Excludes calibration regimes unique to the sensing application
Battery service visit | 35 | £/device/event | Planning allowance |  | Set higher for traffic management, confined space or clinical access
EUR to GBP | 0.85388 | £/€ | ECB, 24 Jul 2026 | https://www.ecb.europa.eu/stats/policy_and_exchange_rates/euro_reference_exchange_rates/html/index.en.html | Update for procurement date
PoE switch/network hardware | 1200 | £/site | Planning allowance |  | Use only incremental switch/UPS capacity attributable to this deployment
PoE switch/network installation | 500 | £/site | Planning allowance |  | Rack, patching, configuration and acceptance; excludes major comms-room works
PoE switch/network support | 120 | £/site/year | Planning allowance |  | Monitoring, firmware and replacement allowance
PoE endpoint commissioning | 20 | £/device | Planning allowance |  | Port configuration, labelling, test and handover
Electricity price | 0.31 | £/kWh | Planning allowance |  | Update to the organisation's delivered electricity rate
PoE power delivery efficiency | 90% | % | Planning allowance | https://ethernetalliance.org/wp-content/uploads/2019/12/WP_EA_Overview8023bt_V2p1_FINAL.pdf | Use measured PSE/cabling efficiency where available
PoE endpoint maintenance | 1 | % of hardware/year | Planning allowance |  | Endpoint-only allowance; switch support is modelled separately
Note on B22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planning placeholder for the incremental PoE-capable switch, UPS and network capacity required by the deployment. Replace with a vendor quote.
Note on B27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planning energy rate. Replace with the organisation's delivered electricity tariff, including applicable levies.

## Category Model
Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO | Category-Level Five-Year TCO
Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns. | Each row is a standalone deployment scenario. Change quantities, sites, device prices, data and battery life in blue columns.
Sensor / use case | Deployment archetype | Units | Sites | LoRa HW £/unit | NB HW £/unit | Install £/unit | NB data MB/month | LoRa battery years | NB battery years | LoRa suitability (1–5) | NB suitability (1–5) | Required behaviour / boundary | Technical recommendation | Evidence confidence | LoRa device capex | LoRa shared infra | LoRa maintenance | LoRa server variable | LoRa TCO | LoRa TCO/unit | NB device & tariff | NB data overage | NB maintenance | NB TCO | NB TCO/unit | LoRa minus NB | Lower-cost option | Saving vs higher TCO | LoRa break-even units/site | Decision note
IAQ sensors | Indoor multi-site | 1069 | 1 | 180 | 195 | 35 | 14.88 | 5 | 3 | 5 | 4 | Periodic CO₂/VOC/PM/temperature metadata | LoRaWAN for dense estates; NB-IoT for isolated buildings | Medium | 245870 | 1125.8 | 56657 | 0 | 303652.8 | 284.05 | 322303.5 | 0 | 58260.5 | 380564 | 356 | -76911.2 | LoRaWAN | 20.21% | 15 | Review coverage, power and support model
Parking bay sensors | Outdoor campus / street |  | 1 | 125 | 140 | 85 | 0.2 | 5 | 4 | 5 | 5 | Occupancy events and health telemetry | LoRaWAN on owned campus; NB-IoT for dispersed street assets | Medium | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Room displays | Indoor rooms |  | 1 | 200 | 220 | 50 | 0.5 | 99 | 99 | 3 | 3 | E-ink/status updates only; not rich interactive content | LoRaWAN for simple e-ink; Wi-Fi/Ethernet for rich displays | Low | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Lux sensors | Indoor multi-site |  | 1 | 70 | 80 | 25 | 0.1 | 8 | 6 | 5 | 4 | Periodic light level and threshold alarms | LoRaWAN where a shared building network exists | Medium | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Metering — electricity and water | Plantrooms / meters |  | 1 | 100 | 110 | 75 | 0.3 | 8 | 6 | 5 | 5 | Registers, pulse counts or Modbus data | LoRaWAN for estates; NB-IoT for utility-style dispersed meters | High | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Fridge / process temperature | Indoor critical assets |  | 1 | 70 | 76 | 45 | 0.5 | 8 | 6 | 5 | 5 | Periodic temperature plus immediate excursion alarm | Either; preserve local logging and alarm path | High | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Waste water monitoring | Remote outdoor assets |  | 1 | 300 | 320 | 250 | 1 | 5 | 4 | 4 | 5 | Level/quality/status metadata; no raw waveforms | NB-IoT usually favoured for dispersed remote assets | Medium | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Water temperature | Remote / plantroom |  | 1 | 85 | 95 | 70 | 0.3 | 8 | 6 | 5 | 5 | Periodic readings and threshold alarms | Either; LoRaWAN when sites share coverage | High | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Water flow | Remote / plantroom |  | 1 | 100 | 110 | 90 | 0.5 | 8 | 6 | 5 | 5 | Pulse/flow total and anomaly alarm | Either; NB-IoT is simpler when widely dispersed | High | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Water leak detection | Indoor dense estate |  | 1 | 65 | 75 | 30 | 0.1 | 5 | 4 | 5 | 5 | Immediate event; local shut-off must not depend on cloud | LoRaWAN for density; NB-IoT for standalone premises | High | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Acoustic sensors | Water / machinery |  | 1 | 150 | 165 | 80 | 2 | 5 | 4 | 4 | 5 | Edge-derived dB/features only; raw audio is unsuitable | NB-IoT for dispersed water loggers; either on campus | Medium | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Bin fill level — ultrasonic | Distributed bins |  | 1 | 124 | 124 | 75 | 0.2 | 8 | 6 | 5 | 5 | Distance/fill percentage and alarms | NB-IoT for citywide assets; LoRaWAN on campus/private estate | High | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Optical bin sensors / computer vision | Distributed bins |  | 1 | 450 | 475 | 180 | 5 | 4 | 3 | 2 | 2 | On-device inference only; do not send images over LPWAN | Use LTE-M/LTE/5G if images are required; LPWAN only for metadata | Low | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Vibration sensors | Plant and machinery |  | 1 | 100 | 110 | 70 | 2 | 5 | 4 | 4 | 4 | Edge-computed RMS/FFT features; raw high-rate waveform unsuitable | Either for features; wired/Wi-Fi/LTE for raw waveform | Medium | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Pressure sensors — medical gases | Clinical plantrooms |  | 1 | 140 | 150 | 180 | 0.5 | 8 | 6 | 4 | 4 | Secondary monitoring only; retain compliant wired alarms | LPWAN may supplement, never replace, the safety alarm system | Low | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled
Ultrasonic non-invasive — medical gases | Clinical cylinders / pipes |  | 1 | 180 | 195 | 200 | 0.5 | 6 | 5 | 4 | 4 | Secondary level/flow telemetry with local fail-safe | Either as supplementary telemetry; validate clinical compliance | Low | 0 | 1125.8 | 0 | 0 | [8 empty] | Not modelled |  |  | Not modelled

## Decision Guide
Decision Guide — LoRaWAN, NB-IoT and PoE
Cost follows architecture. Apply these gates before accepting the cheapest five-year TCO.
Question | LoRaWAN signal | NB-IoT signal | PoE signal | Preferred direction | Risk / caveat | Action
Are devices concentrated in owned buildings/campus? | Strong | Neutral | Strong if cableable | LoRaWAN or PoE | PoE cable routes and switch capacity may dominate cost | RF survey plus structured-cabling and port-capacity survey
Are devices geographically dispersed? | Weak unless public LoRaWAN exists | Strong | Weak | NB-IoT | Carrier coverage varies; PoE usually needs costly civil works | Test target SIM/device and map any existing powered network
Is structured cabling already available near endpoints? | Neutral | Neutral | Strong | PoE | Spare cable does not guarantee spare switch power, UPS or ports | Audit patch panels, port budgets, UPS runtime and VLAN capacity
Is payload small and infrequent? | Strong | Strong | Capable but potentially overbuilt | LoRaWAN or NB-IoT | Architecture overhead can outweigh sensor cost | Define bytes/message, messages/day and alarm bursts
Are images, video, raw audio or raw waveforms required? | Unsuitable | Usually unsuitable | Strong | PoE / wired Ethernet | Cable reach and power class must match the endpoint | Specify bandwidth, power class, storage and cyber controls
Is an immediate local safety action required? | Cloud path insufficient | Cloud path insufficient | Network path still insufficient alone | Local/wired fail-safe | No remote telemetry path should be the sole safety layer | Keep compliant local control and use telemetry for supervision
Will a battery visit be expensive? | Often strongest | Good | No battery at endpoint | PoE if cableable; otherwise compare LPWAN | PoE avoids battery visits but adds cable and switch lifecycle costs | Compare surveyed cable cost with lifetime battery service cost
Do you require frequent two-way control? | Limited downlink capacity | Better but still LPWA | Strong | PoE | Availability now depends on LAN, switch and UPS design | Define latency, redundancy, UPS and recovery requirements
Do you need to avoid local infrastructure? | No | Yes | No | NB-IoT | Recurring carrier dependency replaces gateway/switch ownership | Review contract, roaming, coverage and exit strategy
Is the endpoint more than 100 m of copper path from a switch? | N/A | N/A | Major constraint | Wireless, fibre plus local power, or redesign | Standard twisted-pair Ethernet reach is 100 m | Survey permanent link, patching, containment and surge exposure
Suitability score: 5 = natural fit; 4 = good fit; 3 = conditional; 2 = major constraint; 1 = unsuitable for the stated behaviour.

## Sources
Sources & Evidence Log | Sources & Evidence Log | Sources & Evidence Log | Sources & Evidence Log | Sources & Evidence Log | Sources & Evidence Log
Public sources support the benchmark and technical boundaries. Vendor quotations should replace indicative prices before procurement. | Public sources support the benchmark and technical boundaries. Vendor quotations should replace indicative prices before procurement. | Public sources support the benchmark and technical boundaries. Vendor quotations should replace indicative prices before procurement. | Public sources support the benchmark and technical boundaries. Vendor quotations should replace indicative prices before procurement. | Public sources support the benchmark and technical boundaries. Vendor quotations should replace indicative prices before procurement. | Public sources support the benchmark and technical boundaries. Vendor quotations should replace indicative prices before procurement.
Topic | Evidence used | URL | Accessed | Type | Model impact
NB-IoT tariff | £0.98/device/month plus £0.70 one-off; includes 17 MB/device/month |  | 2026-07-31 | User input | NB recurring connectivity, one-off fee and included-data inputs
NB-IoT overage | £0.01/MB above 17 MB/device/month |  | 2026-07-31 | User input | NB monthly data-overage formula
GBP/EUR | ECB reference rate: £0.85388 per €1 on 24 Jul 2026 | https://www.ecb.europa.eu/stats/policy_and_exchange_rates/euro_reference_exchange_rates/html/index.en.html | 2026-07-27 | Official | Currency conversion
UK NB-IoT reach | BT/EE announced NB-IoT coverage of 97% of UK population | https://newsroom.bt.com/bt-launches-multi-million-pound-nb-iot-network-to-support-uk-smart-cities/ | 2026-07-27 | Operator primary | Supports dispersed-asset option; location testing still required
UK NB-IoT use case | Vodafone NB-IoT supports leak detection without Wi-Fi | https://www.vodafone.co.uk/business/case-studies/leaksafe-and-vodafone-business-narrowband-iot | 2026-07-27 | Operator primary | Leak detection fit
Acoustic water logging | Vodafone says NB-IoT improved underground reach and power versus 3G/4G | https://www.vodafone.co.uk/business/case-studies/nb-iot-gutermann | 2026-07-27 | Operator primary | Acoustic/dispersed water fit
NB-IoT bandwidth boundary | Vodafone describes NB-IoT as supporting small amounts of data | https://www.vodafone.co.uk/business/iot/iot-faqs | 2026-07-27 | Operator primary | Excludes video/raw high-rate data
LoRaWAN smart buildings | LoRa Alliance identifies environmental, leak, occupancy, metering and predictive-maintenance applications | https://lora-alliance.org/buildings-vertical-market/ | 2026-07-27 | Industry body | Building/campus suitability
LoRaWAN/NB-IoT comparison | LoRaWAN evidence for smart buildings and utilities | https://lora-alliance.org/wp-content/uploads/2020/11/cr-lora-102_lorawanr_and_nb-iot.pdf | 2026-07-27 | Industry white paper | Category fit scoring
LoRa gateway | UG65 supports indoor deployments and up to 2,000 devices | https://www.milesight.com/iot/product/lorawan-gateway/ug65 | 2026-07-27 | Vendor primary | Gateway capacity assumption
UK device/gateway pricing | Public UK prices for LoRaWAN, NB-IoT sensors and gateways | https://ukiot.io/shop/ | 2026-07-27 | Distributor | Hardware planning benchmarks
LoRaWAN server | The Things Stack provides managed cloud and free discovery tier | https://www.thethingsindustries.com/stack/plans/ | 2026-07-27 | Vendor primary | Network-server architecture
LoRaWAN server price anchor | AWS Marketplace lists $0.336/hour to register up to 1,000 devices | https://aws.amazon.com/marketplace/pp/prodview-djx65iyt6w5cy | 2026-07-27 | Marketplace | £0.20/device/month planning benchmark at scale
LPWA comparison | GSMA compares bandwidth, latency, battery, spectrum and module cost across NB-IoT and LoRaWAN | https://www.gsma.com/solutions-and-impact/connectivity-for-good/mobile-for-development/wp-content/uploads/2023/04/IoT-for-Development-Use-cases-delivering-impact.pdf | 2026-07-27 | Industry body | Technical decision gates
PoE standards and power classes | IEEE 802.3bt uses all four pairs and extends standardized power delivery | https://standards.ieee.org/ieee/802.3bt/6749/ | 2026-07-31 | Standards body | PoE technical boundary and power-delivery context
PoE copper reach | Standard maximum twisted-pair Ethernet cable length is 100 m | https://www.cisco.com/c/en/us/td/docs/switches/lan/catalyst3750/software/troubleshooting/g_power_over_ethernet.html | 2026-07-31 | Vendor technical guide | Decision gate for cable-route feasibility

## PoE Model
PoE Category-Level Five-Year TCO
PoE is a wired power-and-data architecture. Each row links to the corresponding deployment quantity and site count in Category Model; edit the blue PoE inputs below.
Sensor / use case | Deployment archetype | Units | Sites | PoE HW £/unit | Cabling & install £/unit | Average W/device | PoE suitability (1–5) | Required behaviour / boundary | PoE technical recommendation | Confidence | Endpoint capex | Shared network | Energy, support & maintenance | PoE TCO | PoE TCO/unit
IAQ sensors | Indoor multi-site | 1069 | 1 | 190 | 180 | 4 | 5 | Continuous power and IP data suit fixed indoor IAQ endpoints | PoE is attractive where structured cabling exists; LPWAN remains simpler for retrofit or dispersed sites | High | 416910 | 1700 | 75266.09 | 493876.09 | 462
Parking bay sensors | Outdoor campus / street | 0 | 1 | 160 | 350 | 3 | 2 | Outdoor bay devices need protected cabling and civil works | Use PoE only where ducts and nearby network cabinets already exist | Low
Room displays | Indoor rooms | 0 | 1 | 240 | 160 | 12 | 5 | Rich displays benefit from continuous power and Ethernet bandwidth | PoE is preferred for interactive or frequently updated room displays | High
Lux sensors | Indoor multi-site | 0 | 1 | 85 | 150 | 2 | 5 | Fixed ceiling/wall sensors are compatible with structured cabling | PoE is strong in new-build or refurbished estates with spare ports | High
Metering — electricity and water | Plantrooms / meters | 0 | 1 | 130 | 220 | 4 | 4 | Plantroom meters may be near Ethernet but isolation and interfaces vary | PoE is suitable when meters/controllers are fixed and cabling is practical | Medium
Fridge / process temperature | Indoor critical assets | 0 | 1 | 95 | 180 | 3 | 4 | Fixed critical assets benefit from reliable power and local LAN monitoring | PoE is suitable when cable routing does not compromise hygiene or operations | Medium
Waste water monitoring | Remote outdoor assets | 0 | 1 | 350 | 600 | 6 | 2 | Remote wet environments make copper cabling and surge protection costly | Prefer wireless/cellular unless powered network infrastructure is already present | Low
Water temperature | Remote / plantroom | 0 | 1 | 110 | 250 | 3 | 3 | Plantroom locations may be cableable; remote assets often are not | PoE is conditional on route length, containment and electrical environment | Medium
Water flow | Remote / plantroom | 0 | 1 | 140 | 300 | 4 | 3 | Fixed flow devices may support wired gateways or controllers | PoE is viable on-site but usually weak for geographically dispersed meters | Medium
Water leak detection | Indoor dense estate | 0 | 1 | 90 | 180 | 2 | 4 | Fixed leak sensors can use PoE but cabling cost may exceed device cost | Use PoE for accessible fixed locations; retain local shut-off logic | Medium
Acoustic sensors | Water / machinery | 0 | 1 | 190 | 250 | 5 | 4 | Feature-rich acoustic monitoring benefits from continuous power and bandwidth | PoE is strong for machinery/buildings; cellular remains useful for dispersed water networks | High
Bin fill level — ultrasonic | Distributed bins | 0 | 1 | 180 | 500 | 4 | 2 | Distributed bins rarely have economical Ethernet cabling | Use PoE only for fixed indoor waste points with existing cabling | Low
Optical bin sensors / computer vision | Distributed bins | 0 | 1 | 550 | 350 | 15 | 5 | Images and edge inference need continuous power and higher bandwidth | PoE is the preferred option for cameras and optical sensors within cable reach | High
Vibration sensors | Plant and machinery | 0 | 1 | 150 | 220 | 6 | 5 | High-rate waveform or frequent features benefit from wired bandwidth | PoE is preferred for fixed machinery monitoring where cable routing is safe | High
Pressure sensors — medical gases | Clinical plantrooms | 0 | 1 | 200 | 300 | 5 | 5 | Clinical plantrooms favour supervised wired infrastructure | Use PoE for supplementary telemetry while retaining the compliant alarm system | High
Ultrasonic non-invasive — medical gases | Clinical cylinders / pipes | 0 | 1 | 240 | 300 | 6 | 5 | Fixed clinical cylinder/pipe monitoring benefits from power and deterministic LAN access | PoE is strong for supplementary telemetry; validate isolation and clinical compliance | High

## Checks
Model Checks
One assertion per row. The model status is OK only when all configured calculations tie and all editable cost assumptions are non-negative.
Check | Actual | Expected | Difference | Tolerance | Status | Notes
PoE TCO components tie | 0 | 0 | 0 | 0.01 | OK | Total PoE TCO must equal endpoint capex + shared network + energy/support/maintenance.
Configured PoE rows have unit TCO | 1 | 1 | 0 | 0 | OK | Every row with a device quantity must produce a PoE TCO per unit.
PoE inputs are non-negative | 0.31 | 0 | 0 | 0 | OK | Negative cost, power, suitability or efficiency inputs are not permitted.
Summary category count ties | 16 | 16 | 0 | 0 | OK | Summary must cover all Category Model use cases.
Overall model status |  |  |  |  | OK